System Design Specification (SDS)

Modular Chilled-Water Cooling Plant with Building Management System Integration

ISA/IEC 62443 Target Security Level 3 (SL-T 3) — design of FRS-CHW-001

Template with worked example

Worked example: data center plant — Trane Symbio 800 chiller modules · Rockwell ControlLogix 5580 plant control · Siemens Desigo CC (primary) · Kepware historian (secondary, long-term)

| Field | Value |
| --- | --- |
| Document number | [SDS-CHW-001] |
| Revision | [A — issued for review] |
| Parent documents | [URS-CHW-001 Rev A; FRS-CHW-001 Rev A] |
| Facility | [DC-01 data center, chilled-water plant] |
| Asset owner | [Owner organization] |
| System integrator | [Integrator organization] |
| Prepared by | [Name, role] |
| Date | [DD Month YYYY] |
| Data classification | [Business Confidential] (example marking) |

Vendor settings, product capabilities and catalog references are as of 28 October 2026; confirm them at FAT, SAT and handover.

# Using this template

- Each design element names the FRS rows it implements; Annex A proves every FRS row is designed in this SDS or in the HDS.

- Design decisions record the options considered and why one was chosen, so a project can change a decision knowingly.

- Addresses, VLANs and ports are worked-example values; replace them with the project plan.

- Black text is the template requirement. Blue italic text is the worked example. [Bracketed blue text] is a project fill-in with the worked-example default.

- This template is open source, with no copyright. The Business Confidential marking is an example of the owner’s data classification; replace it with the owner’s own label.

## Approvals

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Asset owner — OT cybersecurity | [Name] |  | [Date] |
| Asset owner — facilities / mechanical engineering | [Name] |  | [Date] |
| System integrator — controls lead | [Name] |  | [Date] |
| System integrator — network and security lead | [Name] |  | [Date] |

## Revision history

| Rev | Date | Description | Author |
| --- | --- | --- | --- |
| [A] | [Date] | [Initial issue for review] | [Name] |

# Contents

1  Purpose and design principles

2  Design decisions

3  Network architecture and addressing

4  Conduit rule register

5  Control software design

6  BMS design (Desigo CC)

7  Historian design (Kepware)

8  Security services design

9  Security configuration baselines per product

10  Role and permission matrix

11  ISA/IEC 62443-3-3 system requirements allocation

12  ISA/IEC 62443-4-2 SAR requirements for systems and software

Annex A  FRS → SDS coverage

Annex B  Open items to confirm

# 1  Purpose and design principles

This System Design Specification (SDS) defines how the functions in FRS-CHW-001 are designed: architecture, network and conduit design, control software structure, BMS and historian design, security services and per-product security configuration baselines. The Hardware Design Specification (HDS) covers the physical hardware; the V&V, commissioning and acceptance work instruction tests both.

Design principles: control stays local and autonomous (chiller, plant controller, skid); supervision is read-mostly; secure protocol variants are used wherever both ends support them; every insecure protocol is confined; SL-A 3 comes from the configured system, with product certification as supporting evidence only.

# 2  Design decisions

| ID | Decision | Options considered | Chosen design and rationale | FRS |
| --- | --- | --- | --- | --- |
| DD-01 | Plant controller architecture | (1) One redundant ControlLogix pair (1756-RM2). (2) Two independent controllers A and B, each owning half of the equipment, with plant-master role failover in logic. | Option 2. Each controller keeps its native OPC UA server for the primary BMS path; OPC UA support under controller redundancy is unconfirmed (OI-03). Losing one controller loses only the units it owns, and the surviving controller takes the plant-master role (staging, TES, economizer) within 10 s. Option 1 remains acceptable if Rockwell confirms OPC UA with redundancy. | FRS-DEG-003, FRS-CHL-006, FRS-INT-003, FRS-CMP-004 |
| DD-02 | Plant-to-BMS integration | (1) Controller-native OPC UA. (2) Data server only. (3) BACnet gateway. | Controller-native OPC UA to Desigo CC (primary); Kepware OPC UA client as read-only secondary feeding the Kepware historian (owner decision). | FRS-INT-003, FRS-INT-004, FRS-HMI-007 |
| DD-03 | Chiller integration | (1) Modbus TCP via MVI56E-MNETC. (2) BACnet/IP to controller via gateway. | Option 1. Each controller polls its own two chillers with an MVI56E-MNETC; writes only from the owning controller; Desigo CC reads chillers over BACnet/SC when Trane supports it, BACnet/IP read-only until then. | FRS-INT-001, FRS-INT-002, FRS-CHL-008 |
| DD-04 | Zone boundaries | (1) One firewall pair for all conduits. (2) Plant boundary pair plus IDMZ pair. | Option 2. FortiGate Rugged 70F HA pair at the plant boundary (Z1–Z4, Z10 ↔ Z5, Z6, Z7); FortiGate 200F HA pair forming the IDMZ (Z8) between OT and Z9. | FRS-NET-001, FRS-NET-002, FRS-NET-004, FRS-NET-005, FRS-SEC-502 |
| DD-05 | Plant control network | (1) Star. (2) DLR ring. (3) PRP. | DLR ring of Stratix 5800 switches in Z2 with each controller, chiller module switch and drive group on its own ring node; recovery inside the 100 ms limit. | FRS-NET-007, FRS-DEG-004 |
| DD-06 | Virtualization | (1) One cluster, port-group separation. (2) Separate host pairs per zone. | Option 2. Two ESXi hosts for Z5 (Desigo CC, Kepware), two for Z7 (infrastructure services); hypervisor management only in Z7. | FRS-SEC-504, FRS-NET-008 |
| DD-07 | Identity | (1) Enterprise domain. (2) Separate OT domain. | Separate OT Active Directory forest in Z7 with no trust to enterprise; Desigo CC, FactoryTalk, Windows hosts, FortiGate and Stratix authenticate to it. | FRS-SEC-101, FRS-SEC-103, FRS-SEC-104, FRS-SEC-107 |
| DD-08 | PKI | (1) Vendor self-signed. (2) Owner two-tier PKI. | Offline root CA (powered off, stored in a safe) and online issuing CA in Z7; CRL published inside OT. | FRS-SEC-108, FRS-SEC-109, FRS-CMP-108, FRS-CMP-109 |
| DD-09 | Time | (1) Enterprise NTP. (2) Local GPS sources. | Two GPS-disciplined NTP appliances in Z7; Stratix 5800 PTP boundary clock in Z2 for CIP Sync to the controllers. | FRS-SEC-211, FRS-CMP-211 |
| DD-10 | Local operator interface | (1) Panel-mounted HMI. (2) FactoryTalk View SE station in Z2. | FactoryTalk View SE local station on a Cincoze CV-100 + P2102 panel PC in Z2, connected to both controllers; independent of Desigo CC. | FRS-HMI-001, FRS-DEG-001 |
| DD-11 | Remote access | (1) Vendor cloud. (2) Owner jump host. | Owner jump host in Z8 with MFA, per-session approval and recording; all vendor cloud connectors disabled. | FRS-SEC-113, FRS-INT-011 |
| DD-12 | Historian | (1) Desigo CC only. (2) Kepware historian long-term. | Kepware historian in Z5 on an encrypted volume as the long-term store (7 years); outbound-only forwarding to campus aggregation through Z8. | FRS-HMI-006, FRS-HMI-007, FRS-DEG-002 |
| DD-13 | Plant-room HVAC | (1) Plant controller. (2) Desigo PXC. | Desigo PXC7 on BACnet/SC in its own zone Z10; refrigerant emergency ventilation stays hardwired. | FRS-PRH-001, FRS-INT-008, FRS-SAF-001 |

# 3  Network architecture and addressing

Zones and conduits are as defined in the URS (section 6) and FRS (section 7).

| Zone | Name | VLAN | Subnet | Boundary |
| --- | --- | --- | --- | --- |
| Z1-1 … Z1-4 | Chiller modules 1–4 | [VLAN 211–214] | [10.20.11.0/28 … 10.20.14.0/28] | Plant boundary FortiGate |
| Z2 | Plant control | [VLAN 220] | [10.20.20.0/24] | Plant boundary FortiGate |
| Z3 | Plant electrical metering | [VLAN 230] | [10.20.30.0/26] | Plant boundary FortiGate |
| Z4 | Vendor packages | [VLAN 240] | [10.20.40.0/26] | Plant boundary FortiGate |
| Z10 | Plant-room HVAC | [VLAN 300] | [10.20.100.0/27] | Plant boundary FortiGate |
| Z5 | BMS supervisory | [VLAN 250] | [10.20.50.0/26] | Plant boundary and IDMZ FortiGates |
| Z6 | Engineering | [VLAN 260] | [10.20.60.0/27] | Plant boundary and IDMZ FortiGates |
| Z7 | OT infrastructure (services) | [VLAN 270] | [10.20.70.0/26] | Plant boundary and IDMZ FortiGates |
| Z7-M | OT infrastructure (management) | [VLAN 271] | [10.20.71.0/26] | Plant boundary FortiGate |
| Z8 | Industrial DMZ | [VLAN 280] | [10.20.80.0/27] | IDMZ FortiGate pair |

The Z2 plant control network is a DLR ring of Stratix 5800 switches (DD-05); chiller module switches and drive groups attach to ring nodes. The Z5, Z6 and Z7 networks run on Catalyst 9300 switches. Every inter-zone path crosses a FortiGate interface; no host is dual-homed across OT zones (FRS-NET-001).

# 4  Conduit rule register (worked example)

Every rule is deny-by-default plus explicit allow; each allow names its FRS justification. Protocol-aware restrictions (read-only function codes and services) apply where the FortiGate signature set supports them (OI-14).

| Rule | Conduit | Source | Destination | Service | Action | Justification |
| --- | --- | --- | --- | --- | --- | --- |
| R-C1-01 | C1-1, C1-2 | Controller A MVI56E-MNETC | Symbio 800 #1, #2 | TCP 502 | Allow | FRS-INT-001 |
| R-C1-02 | C1-3, C1-4 | Controller B MVI56E-MNETC | Symbio 800 #3, #4 | TCP 502 | Allow | FRS-INT-001 |
| R-C9-01 | C9-n | Desigo CC | Symbio 800 #1–#4 | BACnet/SC TCP 443 (when available); else UDP 47808 read-only | Allow | FRS-INT-002 |
| R-C2-01 | C2 | Desigo CC servers | Controllers A, B | TCP 4840 (OPC UA) | Allow | FRS-INT-003 |
| R-C2-02 | C2 | Kepware | Controllers A, B | TCP 4840 (OPC UA) | Allow | FRS-INT-004 |
| R-C3-01 | C3 | EWS | Controllers A, B; PowerFlex 755T | TCP 2221 / UDP 2221 (CIP Security) | Allow | FRS-INT-010, FRS-LCM-004 |
| R-C3-02 | C3 | EWS | Symbio 800, PowerLogic, QuickServer, S7-1500, Desigo PXC | HTTPS 443; ION TLS 7443; vendor tool ports per OI-20 | Allow | FRS-LCM-004 |
| R-C4-01 | C4 | Desigo CC, Kepware | PM8000 | UDP 47808 (read services only where filterable) | Allow | FRS-INT-009 |
| R-C4-02 | C4 | Desigo CC, Kepware | PM5560 | TCP 502 (read function codes only where filterable) | Allow | FRS-INT-009 |
| R-C5-01 | C5 | Controllers A, B MVI56E-MNETC | S7-1500 skid | TCP 502 (read) | Allow | FRS-INT-006 |
| R-C10-01 | C10 | Desigo CC, Kepware | S7-1500 skid | TCP 4840 (OPC UA) | Allow | FRS-INT-005 |
| R-C10-02 | C10 | Desigo CC, Kepware | QuickServer | UDP 47808 (read) | Allow | FRS-INT-007 |
| R-C11-01 | C11 | Desigo PXC | Desigo CC BACnet/SC hub | TCP 443 (BACnet/SC) | Allow | FRS-INT-008 |
| R-C6-01 | C6 | Jump host (Z8) | EWS, Desigo CC clients | RDP 3389 (approved sessions only) | Allow | FRS-SEC-113 |
| R-C6-02 | C6 | Patch / AV staging (Z8) | Z5, Z6, Z7 update services | HTTPS 443 (pull from Z8 by owner services) | Allow | FRS-SEC-302 |
| R-C12-01 | C12 | Kepware historian (Z5) | Campus aggregation forwarder (Z8) | Per SDS 7 (OPC UA or HTTPS), outbound only | Allow | FRS-INT-011 |
| R-C7-01 | C7 | Owner and vendor users (Z9) | Jump host | HTTPS 443 with MFA | Allow | FRS-SEC-113 |
| R-C8-01 | C8 | All OT zones | NTP servers (Z7) | UDP 123 | Allow | FRS-SEC-211 |
| R-C8-02 | C8 | All OT zones | Log collector (Z7) | TCP 6514 (syslog over TLS); UDP 514 only for devices without TLS (listed) | Allow | FRS-SEC-208 |
| R-C8-03 | C8 | Z5, Z6, Z7 hosts; FortiGate; Stratix | Domain controllers (Z7) | LDAPS 636, Kerberos 88, RADIUS 1812, TACACS+ 49 | Allow | FRS-SEC-103 |
| R-C8-04 | C8 | Management hosts (Z7-M) | Switches, FortiGates, ESXi | SSH 22, HTTPS 443, SNMPv3 UDP 161 | Allow | FRS-NET-008 |
| R-C8-05 | C8 | Backup server (Z7) | Z5, Z6 hosts; FortiGate; Stratix | Per backup product; SCP or SFTP for devices | Allow | FRS-SEC-703 |
| R-DEF | All | Any | Any | Any | Deny and log | FRS-NET-002 |

# 5  Control software design

Plant controller program for ControlLogix 5580 controllers A and B, written to the Secure PLC Coding Top 20 (FRS section 10).

| ID | Element | Design (worked example) | FRS |
| --- | --- | --- | --- |
| SW-01 | Task structure | Periodic tasks: Fast 50 ms (I/O conditioning, interlocks, paired-I/O checks); Sequence 250 ms (equipment state machines); Plant 1 s (staging, TES, economizer, master role, calculations); Comms 500 ms (MVI56E-MNETC and OPC UA blocks). Power-up handler and controller fault handler programmed. | FRS-CHL-*, FRS-HYD-*, FRS-CT-*, FRS-ECO-*, FRS-TES-*, FRS-PLC-015, FRS-PLC-016, FRS-PLC-018 |
| SW-02 | Equipment add-on instructions | AOIs: CHL (chiller via Modbus), PMP (pump via CIP), FAN (tower fan), VLV (modulating and two-position valve), FLW (flow and thermal calc), VAL (write validation), ALM (alarm with priority, deadband, delay, shelving). Each AOI version-controlled with a test record. | FRS-PLC-001, FRS-PLC-006, FRS-PLC-007, FRS-PLC-011, FRS-PLC-012, FRS-PLC-020, FRS-MET-002 |
| SW-03 | Plant-master role | Controllers A and B exchange produced/consumed heartbeat tags; A holds the plant-master role by default. If A’s heartbeat is lost for 5 s, B takes the role within 10 s using the last shared plant state; role changes are alarmed P2 and logged. | FRS-DEG-003, FRS-CHL-006, FRS-PLC-004 |
| SW-04 | BMS interface UDTs | BMS_RO (read-only status, alarms), BMS_WRQ (write requests: plant mode, CHW setpoint, demand limit, alarm acknowledge), BMS_VAL (validated values used by logic). Only BMS_WRQ has External Access Read/Write and is exposed for writing on OPC UA; all other tags None or Read Only. | FRS-PLC-008, FRS-PLC-010, FRS-PLC-014, FRS-INT-003, FRS-SEC-305 |
| SW-05 | Write-request handling | Each request carries value and request counter; VAL AOI checks range, rate, mode and role flag, copies accepted values to BMS_VAL, returns status codes, and logs rejected requests with the OPC UA user name supplied by the server diagnostics where available. | FRS-CHL-001, FRS-CHL-007, FRS-SEC-212, FRS-PLC-008 |
| SW-06 | Modes and fail states | Mode state machine per FRS-MOD; retentive mode and setpoint tags; output hold until first full scan validates inputs; drive and valve fail states per FRS-DEG table. | FRS-MOD-*, FRS-DEG-*, FRS-PLC-015, FRS-SEC-306 |
| SW-07 | Integrity and diagnostics | Change detection mask set to logic, tag-value, firmware and mode changes; Audit Value compared with the released value each scan; keyswitch position, controller mode, uptime, scan time, memory use and major faults sent to BMS and trended. | FRS-PLC-002, FRS-PLC-005, FRS-PLC-016, FRS-PLC-017, FRS-PLC-018, FRS-PLC-019, FRS-SEC-304, FRS-HMI-005 |
| SW-08 | Program protection and release | Source protection on released AOIs; firmware and project revision recorded; .ACD and .L5X archived with SHA-256 at each release; MOC number in every change comment. | FRS-PLC-005, FRS-LCM-003, FRS-SEC-703 |
| SW-09 | Communication hygiene | Unused controller services off; MVI56E-MNETC client map limited to listed registers; no Modbus server enabled; OPC UA anonymous off; CIP Security policy from FactoryTalk Policy Manager. | FRS-PLC-013, FRS-PLC-014, FRS-PLC-009, FRS-PLC-003, FRS-SEC-707 |
| SW-10 | Skid program (vendor) | Vendor applies the Top 20 to the S7-1500 program, read-only Modbus data area for the plant, OPC UA server per FRS-INT-005, and declares compliance. | FRS-PLC-021, FRS-WT-* |
| SW-11 | Metering and plant calculations | Thermal load in FLW AOI; efficiency calculated in Desigo CC; meter polling per FRS-MET-001. | FRS-MET-* |
| SW-12 | Safety separation | No safety function is implemented in software. Plant controller monitors refrigerant, fire and permissive signals only; no program path writes to a safety device. | FRS-SAF-* |
| SW-13 | Lifecycle records | Inventory, spares baseline and MOC records maintained in Z7 per SDS 8. | FRS-LCM-* |

# 6  BMS design (Desigo CC)

| ID | Element | Design (worked example) | FRS |
| --- | --- | --- | --- |
| BMS-01 | Server topology | Desigo CC server VM (Windows Server 2026) on the Z5 ESXi pair with a standby option per Siemens supported configuration (confirm); clients on Windows 11 operator stations in Z5. | FRS-HMI-002, FRS-SEC-504 |
| BMS-02 | Users and rights | Desigo CC user groups mapped to OT domain groups per the role matrix (SDS 10); scope rights restrict commands to the BMS_WRQ allowlist. | FRS-SEC-201, FRS-SEC-101, FRS-HMI-002 |
| BMS-03 | Integration drivers | OPC UA client connections to controllers A and B and to the S7-1500 (SignAndEncrypt, owner-PKI certificates); BACnet/SC hub for Desigo PXC and, when available, Symbio 800; BACnet/IP read-only for PM8000, QuickServer and Symbio fallback; Modbus TCP read-only for PM5560 (or via Kepware). | FRS-INT-002, FRS-INT-003, FRS-INT-005, FRS-INT-007, FRS-INT-008, FRS-INT-009, FRS-SEC-301 |
| BMS-04 | Alarms | Four priorities per FRS-HMI-003; alarm attributes from the controller ALM AOI; shelving restricted to Shift Supervisor; security-relevant alarms per FRS-HMI-005. | FRS-HMI-003, FRS-HMI-004, FRS-HMI-005 |
| BMS-05 | Trends and reports | 1-min trends for key analogs, change-of-value for digitals, 13-month retention; daily performance, monthly energy and weekly security reports. | FRS-HMI-006, FRS-HMI-008, FRS-MET-003 |
| BMS-06 | Graphics | Plant overview, chiller, hydronic, tower, economizer, TES, skid, plant-room HVAC and network-health pages; command buttons only for allowlisted requests. | FRS-HMI-002 |

# 7  Historian design (Kepware)

| ID | Element | Design (worked example) | FRS |
| --- | --- | --- | --- |
| HIS-01 | Kepware project | Channels: OPC UA client to controllers A and B and to the S7-1500; BACnet/IP client to PM8000 and QuickServer; Modbus TCP client to PM5560. All tags read-only (client write disabled per channel where supported, and read-only OPC UA user). | FRS-INT-004, FRS-INT-005, FRS-INT-009, FRS-HMI-007 |
| HIS-02 | Kepware historian storage | Critical tags at 1 s, others at 10 s; 7-year retention; storage on an encrypted volume; sizing per OI-17. | FRS-HMI-007, FRS-SEC-401 |
| HIS-03 | Campus aggregation | Outbound-only forwarding from Kepware to the campus aggregation forwarder in Z8 over OPC UA or HTTPS; local buffering during link loss. | FRS-INT-011, FRS-DEG-002 |
| HIS-04 | Kepware hardening | Runtime as a least-privilege service account; user manager with named admins; OPC UA server endpoints (if enabled) SignAndEncrypt only; unused drivers and interfaces removed. | FRS-SEC-201, FRS-SEC-707, FRS-DEV-S204, FRS-DEV-S302 |

# 8  Security services design

| ID | Element | Design (worked example) | FRS |
| --- | --- | --- | --- |
| SVC-01 | Identity | OT AD forest (two DCs, Z7); groups per role; GPOs for password, lockout, banner, screen lock, USB control, application control, audit policy; Windows LAPS; FortiGate and Stratix via RADIUS and TACACS+; jump host MFA. | FRS-SEC-1*, FRS-SEC-201, FRS-SEC-203, FRS-SEC-204, FRS-SEC-205, FRS-SEC-206, FRS-SEC-207 |
| SVC-02 | PKI | Two-tier PKI per DD-08; certificate templates for TLS server, OPC UA application, BACnet/SC device and CIP Security device; validity 2 years; renewal alarm at 60 days. | FRS-SEC-108, FRS-SEC-109, FRS-SEC-403, FRS-CMP-1* |
| SVC-03 | Time | Per DD-09; NTP authentication keys on Stratix and FortiGate; offset monitoring. | FRS-SEC-211 |
| SVC-04 | Logging | Central collector in Z7 receiving syslog over TLS where supported, Windows event forwarding and ESXi syslog; source-silent detection; 12 months online, 3 years archive; read-only API for the owner monitoring function. | FRS-SEC-208, FRS-SEC-209, FRS-SEC-210, FRS-SEC-309, FRS-SEC-601, FRS-CMP-2*, FRS-CMP-3*, FRS-CMP-6* |
| SVC-05 | Malicious code protection | Vendor-qualified endpoint protection or application control on Desigo CC, Kepware, EWS and operator hosts; media scanning station in Z7; FortiGate AV and IPS at C6 and C7. | FRS-SEC-302, FRS-DEV-H302 |
| SVC-06 | Backup and recovery | Backup server in Z7; schedule per FRS-SEC-703; quarterly restore on the test bench; gold images and recovery runbooks per module. | FRS-SEC-703, FRS-SEC-704, FRS-SEC-705, FRS-CMP-7* |
| SVC-07 | Monitoring | Passive OT network monitoring sensors on SPAN ports of the Z1–Z5 and Z10 switches; console in Z7; alerts to the owner security operations function. | FRS-SEC-602, FRS-SEC-202 |
| SVC-08 | Patch and change management | Vendor-qualified patches staged in Z8; applied module by module under MOC; baseline comparison after change. | FRS-SEC-303, FRS-SEC-706, FRS-SEC-708, FRS-DEV-H310, FRS-DEV-E310, FRS-DEV-N310 |
| SVC-09 | Data protection | BitLocker on hosts; encrypted backups; decommissioning procedure; cipher policy. | FRS-SEC-4*, FRS-CMP-4* |
| SVC-10 | Segmentation and boundaries | Per SDS 3 and 4; island-mode policy sets per zone; FortiGate HA without bypass; application control blocks person-to-person protocols; DoS policies per conduit. | FRS-SEC-5*, FRS-SEC-701, FRS-SEC-702, FRS-NET-*, FRS-CMP-5*, FRS-DEV-N* |
| SVC-11 | Physical and component hardening | Per-product baselines in SDS 9; physical controls detailed in the HDS. | FRS-DEV-E*, FRS-DEV-H*, FRS-CMP-0*, FRS-SEC-307, FRS-SEC-308 |

# 9  Security configuration baselines per product

Highlights only; the full baseline for each product is its per-product ISA/IEC 62443 SL-3 checklist, which is also the V&V procedure basis. Exported configurations are compared with these baselines at SAT and after every change (FRS-SEC-706).

| Product | Baseline highlights (worked example) | Checklist |
| --- | --- | --- |
| Trane Symbio 800 | Named Symbio UI users with permissions; HTTPS-only web access; web UI over Ethernet limited to Z6 addresses; Trane Connect off; Air-Fi, Wi-Fi and cellular not fitted; unused protocols (LON) off; BAS communication-loss behaviour set (OI-12); automated encrypted backup on; NTP set. | Symbio 800 (EDR) |
| ControlLogix 5580 (A, B) | Keyswitch RUN with key held by Controls Engineer; FactoryTalk Security; CIP Security via 1756-EN4TR; change detection mask and Audit Value monitoring; web pages off; front USB and SD disabled where supported (OI-13); OPC UA server SignAndEncrypt, anonymous off; External Access per SW-04; CIP Sync time. | ControlLogix 5580 (EDR, Logix capture) |
| ProSoft MVI56E-MNETC | Client map limited to listed registers; no server function; configuration .ppf archived and protected. | ProSoft MVI56E (EDR) |
| PowerFlex 755T | CIP Security policy; communication-loss action Hold Last (OI-13); HIM access physically controlled; parameters in backup and change detection. | PowerFlex 755T (EDR) |
| Danfoss FC 102 | SCF with named accounts and roles; 0-91 integrity check on; 0-92 hash recorded; SNMP (12-83) off unless used; Fire Mode (24-0*) disabled; 8-03 timeout 10 s and 8-04 Freeze output; audit log 43-6* forwarded where possible. | Danfoss FC 102 (EDR) |
| Proline Promag 300/500 | User roles and web server restricted per vendor (OI-05); EtherNet/IP only to Z2 controller; DeviceCare backup. | Promag P300/P500 (EDR) |
| PowerLogic PM8000 | Named accounts, defaults changed; Secure ION (7443) for ION Setup; HTTPS web; unused protocols off; BACnet read-only. | PM8000 (EDR) |
| PowerLogic PM5560 | Firmware 4.x; administrator password changed; HTTPS only with port 80 blocked at the switch ACL; Modbus IP filtering on with two client addresses; display passcodes changed; banner. | PM5560 (EDR) |
| QuickServer PS-QS-3x10-F | Label password changed; HTTPS with owner certificate; users per group; cloud (Grid) registration off; firmware 7.0.0 or later; WAN rules restricted. | QuickServer (NDR) |
| SIMATIC S7-1500 (skid) | Access protection set; user management roles; secure PG/HMI communication; PUT/GET disabled; web server HTTPS only or off; OPC UA SignAndEncrypt, guest off; read-only Modbus server area (OI-15). | S7-1500 (EDR) |
| Desigo PXC7 | BACnet/SC with owner certificates; local web access restricted to Z6; firmware current. | Desigo PXC (EDR) |
| Stratix 5800 | AAA via TACACS+; SSH only; HTTP server off; SNMPv3; storm control; port security and unused ports shut in a parking VLAN; NTP authentication; syslog over TLS where supported; banner; exec-timeout; DLR and PTP per DD-05, DD-09. | Stratix 5800 (NDR) |
| Catalyst 9300 | As Stratix 5800 for IOS-XE management; 802.1X on access ports in Z5 and Z6. | Catalyst 9300 (NDR) |
| FortiGate (FortiOS 7.6) | Deny-all policies per SDS 4; trusted hosts on admins; admin MFA; lockout threshold and duration; strong-crypto; pre-login banner; encrypted configuration backups; HA without bypass; island-mode policy sets; industrial signatures (OI-14). | FortiGate (NDR) |
| Desigo CC V9 (≥ V9.0 QU1) | Domain authentication; scope rights; encrypted client–server communication with owner certificates; OPC UA client SignAndEncrypt; activity log forwarded; cloud connectors off. | Desigo CC (SAR) |
| Kepware | Per HIS-04. | Kepware (SAR) |
| Windows Server 2026 / Windows 11 | OT domain GPOs per SVC-01; BitLocker; Credential Guard; application control; SMBv1 off; RDP NLA; event forwarding. | Windows Server 2026 / Windows 11 (HDR) |
| VMware ESXi 8 | Lockdown mode; SSH and shell off; Security.AccountLockFailures and AccountUnlockTime; Security.PasswordQualityControl; Syslog.global.logHost; Secure Boot with execInstalledOnly; TPM attestation; management only from Z7-M. | VMware ESXi 8 (HDR) |

# 10  Role and permission matrix

| Function | Viewer | Plant Operator | Shift Supervisor | Plant Engineer | Controls Engineer | Security Admin | Vendor Service |
| --- | --- | --- | --- | --- | --- | --- | --- |
| View plant, alarms, trends | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ (session) |
| Acknowledge alarms |  | ✓ | ✓ | ✓ | ✓ |  |  |
| Request setpoint / demand limit |  | ✓ | ✓ | ✓ | ✓ |  |  |
| Enter Emergency mode |  |  | ✓ | ✓ | ✓ |  |  |
| Manual unit control, maintenance lockout |  |  |  | ✓ | ✓ |  |  |
| Shelve alarms |  |  | ✓ | ✓ |  |  |  |
| Change controller logic or device configuration |  |  |  |  | ✓ |  | ✓ (approved session) |
| Change firewall, switch, identity or PKI configuration |  |  |  |  |  | ✓ |  |

# 11  ISA/IEC 62443-3-3 system requirements allocation

Every system requirement at SL-T 3, with its requirement enhancements as stated in the URS, allocated to the design elements that meet it and the points where it is enforced.

| Ref. | Requirement | Design elements | Enforcement points | URS | FRS |
| --- | --- | --- | --- | --- | --- |
| FR 1 — Identification and authentication control (IAC) |  |  |  |  |  |
| SR 1.1 | Human user identification and authentication | SVC-01, DD-07, DD-11, BMS-02; HDS PH-05 | All interactive interfaces; jump host MFA in Z8 | URS-S-101 | FRS-SEC-101 |
| SR 1.2 | Software process and device identification and authentication | DD-08, SVC-02, BMS-03, HIS-01, rule register (address pinning) | C1–C12; Z2 CIP Security | URS-S-102 | FRS-SEC-102 |
| SR 1.3 | Account management | DD-07, SVC-01 | Z7 directory; device account register | URS-S-103 | FRS-SEC-103 |
| SR 1.4 | Identifier management | SVC-01 | Z7 directory | URS-S-104 | FRS-SEC-104 |
| SR 1.5 | Authenticator management | SVC-01, SVC-02, SDS 9 baselines; HDS HS-01 | All components | URS-S-105 | FRS-SEC-105 |
| SR 1.6 | Wireless access management | SDS 9 baselines; HDS PH-06 | Z1–Z10 | URS-S-106 | FRS-SEC-106 |
| SR 1.7 | Strength of password-based authentication | SVC-01, SDS 9 | Directory, FortiGate, switches, ESXi | URS-S-107 | FRS-SEC-107 |
| SR 1.8 | Public key infrastructure certificates | DD-08, SVC-02 | Z7 PKI; all TLS, OPC UA, BACnet/SC, CIP Security endpoints | URS-S-108 | FRS-SEC-108 |
| SR 1.9 | Strength of public key authentication | DD-08, SVC-02 | Z7 CRL | URS-S-109 | FRS-SEC-109 |
| SR 1.10 | Authenticator feedback | SDS 9 | All interfaces | URS-S-110 | FRS-SEC-110 |
| SR 1.11 | Unsuccessful login attempts | SVC-01, SDS 9 | Directory, FortiGate, ESXi, QuickServer, FC 102 | URS-S-111 | FRS-SEC-111 |
| SR 1.12 | System use notification | SVC-01, SDS 9 | All supporting interfaces | URS-S-112 | FRS-SEC-112 |
| SR 1.13 | Access via untrusted networks | DD-11, rules R-C6-01, R-C7-01 | Z8 jump host; FortiGate 200F pair | URS-S-113 | FRS-SEC-113 |
| FR 2 — Use control (UC) |  |  |  |  |  |
| SR 2.1 | Authorization enforcement | SDS 10, BMS-02, SW-04, HIS-04 | Every application and device | URS-S-201 | FRS-SEC-201 |
| SR 2.2 | Wireless use control | SVC-07; HDS PH-06 | Plant room and panels | URS-S-202 | FRS-SEC-202 |
| SR 2.3 | Use control for portable and mobile devices | SVC-01; HDS PH-04, hardware features table | EWS, panels, controllers | URS-S-203 | FRS-SEC-203 |
| SR 2.4 | Mobile code | SVC-01, SVC-05 | Z5, Z6, Z7 hosts | URS-S-204 | FRS-SEC-204 |
| SR 2.5 | Session lock | SVC-01 | Workstations and consoles | URS-S-205 | FRS-SEC-205 |
| SR 2.6 | Remote session termination | SVC-01, DD-11 | Jump host, FortiGate, switches, ESXi | URS-S-206 | FRS-SEC-206 |
| SR 2.7 | Concurrent session control | SVC-01, HIS-04 | Controllers, FortiGate, applications | URS-S-207 | FRS-SEC-207 |
| SR 2.8 | Auditable events | SVC-04, SW-07 | All sources → Z7 collector | URS-S-208 | FRS-SEC-208 |
| SR 2.9 | Audit storage capacity | SVC-04 | Z7 collector | URS-S-209 | FRS-SEC-209 |
| SR 2.10 | Response to audit processing failures | SVC-04, BMS-04 | Z7 collector; operator alarms | URS-S-210 | FRS-SEC-210 |
| SR 2.11 | Timestamps | DD-09, SVC-03; HDS NW-07 | Z7 NTP; Z2 PTP | URS-S-211 | FRS-SEC-211 |
| SR 2.12 | Non-repudiation | SW-05, SW-08, SVC-01 | Controllers, BMS, firewall change records | URS-S-212 | FRS-SEC-212 |
| FR 3 — System integrity (SI) |  |  |  |  |  |
| SR 3.1 | Communication integrity | DD-02, DD-03, BMS-03, HIS-01, protocol table | All conduits | URS-S-301 | FRS-SEC-301 |
| SR 3.2 | Malicious code protection | SVC-05 | Hosts; C6, C7 | URS-S-302 | FRS-SEC-302 |
| SR 3.3 | Security functionality verification | SVC-08 | All components | URS-S-303 | FRS-SEC-303 |
| SR 3.4 | Software and information integrity | SW-07, SW-08, SVC-08 | Controllers, drives, hosts | URS-S-304 | FRS-SEC-304 |
| SR 3.5 | Input validation | SW-04, SW-05 | Plant controllers | URS-S-305 | FRS-SEC-305 |
| SR 3.6 | Deterministic output | SW-06; HDS section 5 | Final elements | URS-S-306 | FRS-SEC-306 |
| SR 3.7 | Error handling | SDS 9 | Web and OPC UA endpoints | URS-S-307 | FRS-SEC-307 |
| SR 3.8 | Session integrity | SDS 9 | Web and OPC UA endpoints | URS-S-308 | FRS-SEC-308 |
| SR 3.9 | Protection of audit information | SVC-04 | Z7 collector | URS-S-309 | FRS-SEC-309 |
| FR 4 — Data confidentiality (DC) |  |  |  |  |  |
| SR 4.1 | Information confidentiality | SVC-09, HIS-02 | Backups, volumes, transport | URS-S-401 | FRS-SEC-401 |
| SR 4.2 | Information persistence | SVC-09; HDS EN-05 | Decommissioning | URS-S-402 | FRS-SEC-402 |
| SR 4.3 | Use of cryptography | SVC-02, SVC-09, SDS 9 | All TLS and OPC UA endpoints | URS-S-403 | FRS-SEC-403 |
| FR 5 — Restricted data flow (RDF) |  |  |  |  |  |
| SR 5.1 | Network segmentation | DD-04, DD-05, SDS 3 | Physical plant network | URS-S-501 | FRS-SEC-501 |
| SR 5.2 | Zone boundary protection | DD-04, rule register, SVC-10 | FortiGate pairs | URS-S-502 | FRS-SEC-502 |
| SR 5.3 | General purpose person-to-person communication restrictions | SVC-10 | FortiGate application control | URS-S-503 | FRS-SEC-503 |
| SR 5.4 | Application partitioning | DD-06, SDS 3 | ESXi host pairs, VLANs | URS-S-504 | FRS-SEC-504 |
| FR 6 — Timely response to events (TRE) |  |  |  |  |  |
| SR 6.1 | Audit log accessibility | SVC-04 | Z7 collector API | URS-S-601 | FRS-SEC-601 |
| SR 6.2 | Continuous monitoring | SVC-07; HDS NW-05 | SPAN or TAP sensors | URS-S-602 | FRS-SEC-602 |
| FR 7 — Resource availability (RA) |  |  |  |  |  |
| SR 7.1 | Denial of service protection | SVC-10, DD-05 | Stratix storm control; FortiGate DoS | URS-S-701 | FRS-SEC-701 |
| SR 7.2 | Resource management | SW-07, HIS-04 | Controllers, hosts | URS-S-702 | FRS-SEC-702 |
| SR 7.3 | Control system backup | SVC-06, SW-08 | Z7 backup server | URS-S-703 | FRS-SEC-703 |
| SR 7.4 | Control system recovery and reconstitution | SVC-06; HDS EN-04 | Spares, gold images | URS-S-704 | FRS-SEC-704 |
| SR 7.5 | Emergency power | SVC-06; HDS PW-01, PW-03 | UPS, restart behaviour | URS-S-705 | FRS-SEC-705 |
| SR 7.6 | Network and security configuration settings | SDS 9, SVC-08 | All components | URS-S-706 | FRS-SEC-706 |
| SR 7.7 | Least functionality | SW-09, SDS 9; HDS NW-03 | All components | URS-S-707 | FRS-SEC-707 |
| SR 7.8 | Control system component inventory | SVC-08; HDS EN-03 | Z7 inventory | URS-S-708 | FRS-SEC-708 |

# 12  ISA/IEC 62443-4-2 SAR requirements for systems and software

Every software application in the system shall meet each requirement below at SL-C 3, including the requirement enhancements specified for SL 3, by capability or by the named compensation (URS-C-002). The host each application runs on is a separate HDR (HDS section 12).

## 12.1  Software inventory

| Tag | Software | Zone | Checklist |
| --- | --- | --- | --- |
| SW-DCC | Desigo CC V9 (≥ V9.0 QU1) | Z5 | Desigo CC (library) |
| SW-KEP | Kepware with Kepware historian | Z5 | Kepware (library) |
| SW-S5K | Studio 5000 Logix Designer, FactoryTalk Security, Policy Manager, Linx | Z6 | Studio 5000; FactoryTalk (library) |
| SW-FTV | FactoryTalk View SE (local station and development) | Z2, Z6 | FactoryTalk (library) |
| SW-TIA | TIA Portal (skid engineering) | Z6 / vendor | New checklist needed |
| SW-TTU | Trane Tracer TU | Z6 | New checklist needed |
| SW-MCT | Danfoss MCT 10 | Z6 | New checklist needed |
| SW-DVC | Endress+Hauser DeviceCare / FieldCare | Z6 | New checklist needed |
| SW-ION | Schneider ION Setup | Z6 | ION Setup (library) |
| SW-PCB | ProSoft Configuration Builder | Z6 | New checklist needed |
| SW-ABT | Siemens Desigo ABT (PXC engineering) | Z6 | New checklist needed |
| SW-OWN | Owner services: log collector, monitoring console, backup, jump host and recording, endpoint protection, AD CS | Z7, Z8 | Per selected product |

## 12.2  Requirements

| Ref. | Requirement | Applies to | Design realization (worked example) | Software-specific gaps and compensation | FRS |
| --- | --- | --- | --- | --- | --- |
| Component requirements (all component types) |  |  |  |  |  |
| CR 1.1 | Human user identification and authentication | All SAR | Desigo CC, Kepware, FactoryTalk and owner services authenticate named domain users; engineering tools run under named domain logons. | Vendor engineering tools without their own login (e.g., Tracer TU, MCT 10, DeviceCare, PCB) → host login plus device-side authentication. | FRS-CMP-101 |
| CR 1.2 | Software process and device identification and authentication | All SAR | OPC UA application certificates (Desigo CC, Kepware); BACnet/SC (Desigo CC); FactoryTalk Linx with CIP Security. | Tools using unauthenticated device protocols → Z6-only conduit (R-C3). | FRS-CMP-102 |
| CR 1.3 | Account management | All SAR | Accounts and groups in the OT domain; application roles mapped to groups. | — | FRS-CMP-103 |
| CR 1.4 | Identifier management | All SAR | Unique identifiers; service accounts per application. | — | FRS-CMP-104 |
| CR 1.5 | Authenticator management | All SAR | Service account passwords vaulted; certificates from owner PKI. | — | FRS-CMP-105 |
| CR 1.7 | Strength of password-based authentication | All SAR | Domain policy applies to application logons. | — | FRS-CMP-107 |
| CR 1.8 | Public key infrastructure certificates | All SAR | Owner-PKI certificates for Desigo CC, Kepware, FactoryTalk and owner services. | — | FRS-CMP-108 |
| CR 1.9 | Strength of public key-based authentication | All SAR | Trust lists and CRL checking in OPC UA and TLS stacks. | — | FRS-CMP-109 |
| CR 1.10 | Authenticator feedback | All SAR | Masked entry. | — | FRS-CMP-110 |
| CR 1.11 | Unsuccessful login attempts | All SAR | Domain lockout; application lockout where native. | — | FRS-CMP-111 |
| CR 1.12 | System use notification | All SAR | Host banner; application banner where supported. | — | FRS-CMP-112 |
| CR 1.14 | Strength of symmetric key-based authentication | All SAR | No hard-coded symmetric keys; secrets in application vaults. | — | FRS-CMP-114 |
| CR 2.1 | Authorization enforcement | All SAR | Role mapping per SDS 10 (Desigo CC scope rights, FactoryTalk Security permissions, Kepware user manager, read-only Kepware OPC UA user). | — | FRS-CMP-201 |
| CR 2.2 | Wireless use control | All SAR | Not applicable — no wireless function in the applications. | — | FRS-CMP-202 |
| CR 2.5 | Session lock | All SAR | Client session lock and timeout. | — | FRS-CMP-205 |
| CR 2.6 | Remote session termination | All SAR | Remote session termination via jump host and application timeouts. | — | FRS-CMP-206 |
| CR 2.7 | Concurrent session control | All SAR | Concurrent session limits per user. | — | FRS-CMP-207 |
| CR 2.8 | Auditable events | All SAR | Desigo CC activity log, FactoryTalk audit, Kepware event log, owner services logs → collector. | Engineering tools with limited logging → host logs and MOC records. | FRS-CMP-208 |
| CR 2.9 | Audit storage capacity | All SAR | Application log retention set; collector capacity. | — | FRS-CMP-209 |
| CR 2.10 | Response to audit processing failures | All SAR | Application keeps running if logging fails; alarm raised. | — | FRS-CMP-210 |
| CR 2.11 | Timestamps | All SAR | Host time from OT NTP. | — | FRS-CMP-211 |
| CR 2.12 | Non-repudiation | All SAR | Named users on every change; MOC comments. | — | FRS-CMP-212 |
| CR 3.1 | Communication integrity | All SAR | OPC UA SignAndEncrypt, BACnet/SC, TLS client–server encryption. | — | FRS-CMP-301 |
| CR 3.3 | Security functionality verification | All SAR | Configuration export and comparison. | — | FRS-CMP-303 |
| CR 3.4 | Software and information integrity | All SAR | Signed installers; file-integrity monitoring of application folders. | — | FRS-CMP-304 |
| CR 3.5 | Input validation | All SAR | Applications validate operator input; controller validates again (FRS-PLC-008). | — | FRS-CMP-305 |
| CR 3.6 | Deterministic output | All SAR | Applications fail without affecting plant control. | — | FRS-CMP-306 |
| CR 3.7 | Error handling | All SAR | Generic error messages. | — | FRS-CMP-307 |
| CR 3.8 | Session integrity | All SAR | Unique session identifiers, invalidated at logout. | — | FRS-CMP-308 |
| CR 3.9 | Protection of audit information | All SAR | Logs forwarded; local log access restricted. | — | FRS-CMP-309 |
| CR 4.1 | Information confidentiality | All SAR | Project, configuration and historian data on encrypted storage. | — | FRS-CMP-401 |
| CR 4.2 | Information persistence | All SAR | Application data purged at decommissioning. | — | FRS-CMP-402 |
| CR 4.3 | Use of cryptography | All SAR | Current algorithms only; deprecated OPC UA policies disabled. | — | FRS-CMP-403 |
| CR 5.1 | Network segmentation | All SAR | Applications installed only in their zone (SDS 3). | — | FRS-CMP-501 |
| CR 6.1 | Audit log accessibility | All SAR | Logs exportable programmatically. | — | FRS-CMP-601 |
| CR 6.2 | Continuous monitoring | All SAR | Application events monitored via collector. | — | FRS-CMP-602 |
| CR 7.1 | Denial of service protection | All SAR | Client connection limits; controller OPC UA load managed. | — | FRS-CMP-701 |
| CR 7.2 | Resource management | All SAR | Resource use monitored. | — | FRS-CMP-702 |
| CR 7.3 | Control system backup | All SAR | Project and database backups (SVC-06). | — | FRS-CMP-703 |
| CR 7.4 | Control system recovery and reconstitution | All SAR | Reinstall and restore runbooks. | — | FRS-CMP-704 |
| CR 7.6 | Network and security configuration settings | All SAR | Hardening per vendor guides and checklists. | — | FRS-CMP-706 |
| CR 7.7 | Least functionality | All SAR | Unused modules, drivers and interfaces removed. | — | FRS-CMP-707 |
| CR 7.8 | Control system component inventory | All SAR | Versions and patch levels in the inventory; SBOM where supplied. | — | FRS-CMP-708 |
| SAR-specific requirements |  |  |  |  |  |
| SAR 2.4 | Mobile code | All SAR | Desigo CC and Kepware clients only on managed hosts. | — | FRS-DEV-S204 |
| SAR 3.2 | Protection from malicious code | All SAR | Desigo CC, Kepware and Studio 5000 run with vendor-qualified protection on their hosts. | — | FRS-DEV-S302 |

Applies to: SW-DCC, SW-KEP, SW-S5K, SW-FTV, SW-TIA, SW-TTU, SW-MCT, SW-DVC, SW-ION, SW-PCB, SW-ABT, SW-OWN.

# Annex A  FRS → SDS coverage

Generated from the FRS and SDS data (and the HDS where present). FRS rows designed in neither document: none.

| FRS row | SDS elements | HDS elements |
| --- | --- | --- |
| FRS-CHL-001 | SW-01, SW-05 | — |
| FRS-CHL-002 | SW-01 | CH-n-EN, CH-n-RUN, FS-CHW-n / FS-CW-n |
| FRS-CHL-003 | SW-01 | — |
| FRS-CHL-004 | SW-01 | — |
| FRS-CHL-005 | SW-01 | — |
| FRS-CHL-006 | DD-01, SW-01, SW-03 | — |
| FRS-CHL-007 | SW-01, SW-05 | — |
| FRS-CHL-008 | DD-03, SW-01 | — |
| FRS-HYD-001 | SW-01 | P-CHW-1…4 |
| FRS-HYD-002 | SW-01 | HDS-5 Minimum-flow bypass valve |
| FRS-HYD-003 | SW-01 | — |
| FRS-HYD-004 | SW-01 | — |
| FRS-HYD-005 | SW-01 | P-CW-1…4 |
| FRS-CT-001 | SW-01 | F-CT-1…4 |
| FRS-CT-002 | SW-01 | — |
| FRS-CT-003 | SW-01 | F-CT-1…4, VIB-CT-n |
| FRS-CT-004 | SW-01 | HDS-5 Tower bypass valve |
| FRS-ECO-001 | SW-01 | — |
| FRS-ECO-002 | SW-01 | HDS-5 Economizer HX valves |
| FRS-ECO-003 | SW-01 | — |
| FRS-TES-001 | SW-01 | TES-DV, HDS-5 TES discharge valve |
| FRS-TES-002 | SW-01 | — |
| FRS-TES-003 | SW-01 | — |
| FRS-WT-001 | SW-10 | WT-1 |
| FRS-WT-002 | SW-10 | WT-1 |
| FRS-PRH-001 | DD-13 | PXC-1 |
| FRS-MET-001 | SW-11 | M-CH-1…4, M-MCC-1…4 |
| FRS-MET-002 | SW-02, SW-11 | FT-CHW-1, 2 |
| FRS-MET-003 | SW-11, BMS-05 | — |
| FRS-MOD-001 | SW-06, SDS-10 | — |
| FRS-MOD-002 | SW-06 | — |
| FRS-MOD-003 | SW-06 | — |
| FRS-MOD-004 | SW-06 | — |
| FRS-DEG-001 | DD-10, SW-06 | — |
| FRS-DEG-002 | DD-12, SW-06, HIS-03 | — |
| FRS-DEG-003 | DD-01, SW-03, SW-06 | CP-A, CP-B, PLC-A, PLC-B, HDS-3, PW-04 |
| FRS-DEG-004 | DD-05, SW-06 | NW-01, EN-01 |
| FRS-DEG-005 | SW-06 | UPS-C, UPS-ALM, PSU-ALM, PW-01, PW-02, PW-03 |
| FRS-DEG-006 | SW-06 | TES-DV, HDS-5 Chiller isolation valves, HDS-5 Minimum-flow bypass valve, HDS-5 Economizer HX valves, HDS-5 TES discharge valve, HDS-5 Tower bypass valve |
| FRS-SAF-001 | DD-13, SW-12 | RM-1, RM-ALM |
| FRS-SAF-002 | SW-12 | — |
| FRS-SAF-003 | SW-12 | FA-SD |
| FRS-SAF-004 | SW-12 | HDS-10 PowerFlex 755T / FC 102 |
| FRS-SAF-005 | SW-12 | — |
| FRS-SAF-006 | SW-12 | CH-n-EN, FS-CHW-n / FS-CW-n, ES-PLANT |
| FRS-LCM-001 | SW-13 | — |
| FRS-LCM-002 | SW-13 | EN-04 |
| FRS-LCM-003 | SW-08, SW-13 | — |
| FRS-LCM-004 | R-C3-01, R-C3-02, SW-13 | EWS-1, 2 |
| FRS-HMI-001 | DD-10 | OIS-1, HDS-3 |
| FRS-HMI-002 | BMS-01, BMS-02, BMS-06 | — |
| FRS-HMI-003 | BMS-04 | — |
| FRS-HMI-004 | BMS-04, SDS-10 | — |
| FRS-HMI-005 | SW-07, BMS-04 | — |
| FRS-HMI-006 | DD-12, BMS-05 | — |
| FRS-HMI-007 | DD-02, DD-12, HIS-01, HIS-02 | HS-02 |
| FRS-HMI-008 | BMS-05 | — |
| FRS-INT-001 | DD-03, R-C1-01, R-C1-02 | MB-A, MB-B, HDS-3 |
| FRS-INT-002 | DD-03, R-C9-01, BMS-03 | — |
| FRS-INT-003 | DD-01, DD-02, R-C2-01, SW-04, BMS-03 | PLC-A, PLC-B |
| FRS-INT-004 | DD-02, R-C2-02, HIS-01 | — |
| FRS-INT-005 | R-C10-01, BMS-03, HIS-01 | — |
| FRS-INT-006 | R-C5-01 | WT-TRIP |
| FRS-INT-007 | R-C10-02, BMS-03 | GW-1 |
| FRS-INT-008 | DD-13, R-C11-01, BMS-03 | PXC-1 |
| FRS-INT-009 | R-C4-01, R-C4-02, BMS-03, HIS-01 | — |
| FRS-INT-010 | R-C3-01 | EN-A1, EN-B1, P-CHW-1…4, HDS-3 |
| FRS-INT-011 | DD-11, R-C12-01, HIS-03 | — |
| FRS-INT-012 | — | WT-TRIP, HDS-4, PW-04 |
| FRS-NET-001 | DD-04, SDS-3, SVC-10 | SW-C1, C2, NW-02, EN-03 |
| FRS-NET-002 | DD-04, R-DEF, SVC-10 | FW-P1, P2, NW-04 |
| FRS-NET-003 | SVC-10 | — |
| FRS-NET-004 | DD-04, SVC-10 | — |
| FRS-NET-005 | DD-04, SVC-10 | FW-P1, P2, FW-D1, D2, NW-04 |
| FRS-NET-006 | SVC-10 | — |
| FRS-NET-007 | DD-05, SDS-3, SVC-10 | EN-A1, EN-B1, SW-R1…R6, NW-01, EN-02 |
| FRS-NET-008 | DD-06, R-C8-04, SVC-10 | NW-06, HS-03 |
| FRS-SEC-101 | DD-07, BMS-02, SVC-01, SDS-11 SR 1.1 | PH-05 |
| FRS-SEC-102 | SVC-01, SDS-11 SR 1.2 | — |
| FRS-SEC-103 | DD-07, R-C8-03, SVC-01, SDS-11 SR 1.3 | — |
| FRS-SEC-104 | DD-07, SVC-01, SDS-11 SR 1.4 | — |
| FRS-SEC-105 | SVC-01, SDS-11 SR 1.5 | HS-01 |
| FRS-SEC-106 | SVC-01, SDS-11 SR 1.6 | CH-1…4, PH-06 |
| FRS-SEC-107 | DD-07, SVC-01, SDS-11 SR 1.7 | — |
| FRS-SEC-108 | DD-08, SVC-01, SVC-02, SDS-11 SR 1.8 | — |
| FRS-SEC-109 | DD-08, SVC-01, SVC-02, SDS-11 SR 1.9 | — |
| FRS-SEC-110 | SVC-01, SDS-11 SR 1.10 | — |
| FRS-SEC-111 | SVC-01, SDS-11 SR 1.11 | — |
| FRS-SEC-112 | SVC-01, SDS-11 SR 1.12 | — |
| FRS-SEC-113 | DD-11, R-C6-01, R-C7-01, SVC-01, SDS-11 SR 1.13 | FW-D1, D2, JH-1 |
| FRS-SEC-201 | BMS-02, HIS-04, SVC-01, SDS-10, SDS-11 SR 2.1 | — |
| FRS-SEC-202 | SVC-07, SDS-11 SR 2.2 | PH-06 |
| FRS-SEC-203 | SVC-01, SDS-11 SR 2.3 | PH-01, PH-04, HDS-10 ControlLogix 5580 |
| FRS-SEC-204 | SVC-01, SDS-11 SR 2.4 | — |
| FRS-SEC-205 | SVC-01, SDS-11 SR 2.5 | — |
| FRS-SEC-206 | SVC-01, SDS-11 SR 2.6 | — |
| FRS-SEC-207 | SVC-01, SDS-11 SR 2.7 | — |
| FRS-SEC-208 | R-C8-02, SVC-04, SDS-11 SR 2.8 | — |
| FRS-SEC-209 | SVC-04, SDS-11 SR 2.9 | — |
| FRS-SEC-210 | SVC-04, SDS-11 SR 2.10 | — |
| FRS-SEC-211 | DD-09, R-C8-01, SVC-03, SDS-11 SR 2.11 | SW-R1…R6, NTP-1, 2, NW-07 |
| FRS-SEC-212 | SW-05, SDS-11 SR 2.12 | — |
| FRS-SEC-301 | BMS-03, SDS-11 SR 3.1 | — |
| FRS-SEC-302 | R-C6-02, SVC-05, SDS-11 SR 3.2 | — |
| FRS-SEC-303 | SVC-08, SDS-11 SR 3.3 | — |
| FRS-SEC-304 | SW-07, SDS-11 SR 3.4 | HDS-10 ControlLogix 5580 |
| FRS-SEC-305 | SW-04, SDS-11 SR 3.5 | — |
| FRS-SEC-306 | SW-06, SDS-11 SR 3.6 | — |
| FRS-SEC-307 | SVC-11, SDS-11 SR 3.7 | — |
| FRS-SEC-308 | SVC-11, SDS-11 SR 3.8 | — |
| FRS-SEC-309 | SVC-04, SDS-11 SR 3.9 | — |
| FRS-SEC-401 | HIS-02, SVC-09, SDS-11 SR 4.1 | HS-02 |
| FRS-SEC-402 | SVC-09, SDS-11 SR 4.2 | EN-05 |
| FRS-SEC-403 | SVC-02, SVC-09, SDS-11 SR 4.3 | — |
| FRS-SEC-501 | SDS-3, SVC-10, SDS-11 SR 5.1 | — |
| FRS-SEC-502 | DD-04, SVC-10, SDS-11 SR 5.2 | — |
| FRS-SEC-503 | SVC-10, SDS-11 SR 5.3 | — |
| FRS-SEC-504 | DD-06, BMS-01, SVC-10, SDS-11 SR 5.4 | ESX-5A, 5B, ESX-7A, 7B |
| FRS-SEC-601 | SVC-04, SDS-11 SR 6.1 | — |
| FRS-SEC-602 | SVC-07, SDS-11 SR 6.2 | MON-1…n, NW-05 |
| FRS-SEC-701 | SVC-10, SDS-11 SR 7.1 | — |
| FRS-SEC-702 | SVC-10, SDS-11 SR 7.2 | — |
| FRS-SEC-703 | R-C8-05, SW-08, SVC-06, SDS-11 SR 7.3 | — |
| FRS-SEC-704 | SVC-06, SDS-11 SR 7.4 | EN-04 |
| FRS-SEC-705 | SVC-06, SDS-11 SR 7.5 | UPS-C, PW-01, PW-03 |
| FRS-SEC-706 | SVC-08, SDS-9, SDS-11 SR 7.6 | — |
| FRS-SEC-707 | SW-09, HIS-04, SDS-11 SR 7.7 | NW-03 |
| FRS-SEC-708 | SVC-08, SDS-11 SR 7.8 | EN-03 |
| FRS-CMP-001 | SVC-11, SDS-9 | — |
| FRS-CMP-002 | SVC-11, SDS-9 | — |
| FRS-CMP-003 | SVC-11, SDS-9 | — |
| FRS-CMP-004 | DD-01, SVC-11, SDS-9 | — |
| FRS-CMP-005 | SVC-11, SDS-9 | — |
| FRS-CMP-101 | SVC-02, SDS-9, SDS-12 CR 1.1 | PH-05, HDS-12 EDR CR 1.1, HDS-12 HDR CR 1.1, HDS-12 NDR CR 1.1 |
| FRS-CMP-102 | SVC-02, SDS-9, SDS-12 CR 1.2 | HDS-12 EDR CR 1.2, HDS-12 HDR CR 1.2, HDS-12 NDR CR 1.2 |
| FRS-CMP-103 | SVC-02, SDS-9, SDS-12 CR 1.3 | HDS-12 EDR CR 1.3, HDS-12 HDR CR 1.3, HDS-12 NDR CR 1.3 |
| FRS-CMP-104 | SVC-02, SDS-9, SDS-12 CR 1.4 | HDS-12 EDR CR 1.4, HDS-12 HDR CR 1.4, HDS-12 NDR CR 1.4 |
| FRS-CMP-105 | SVC-02, SDS-9, SDS-12 CR 1.5 | HDS-12 EDR CR 1.5, HDS-12 HDR CR 1.5, HDS-12 NDR CR 1.5 |
| FRS-CMP-107 | SVC-02, SDS-9, SDS-12 CR 1.7 | HDS-12 EDR CR 1.7, HDS-12 HDR CR 1.7, HDS-12 NDR CR 1.7 |
| FRS-CMP-108 | DD-08, SVC-02, SDS-9, SDS-12 CR 1.8 | HDS-12 EDR CR 1.8, HDS-12 HDR CR 1.8, HDS-12 NDR CR 1.8 |
| FRS-CMP-109 | DD-08, SVC-02, SDS-9, SDS-12 CR 1.9 | HDS-12 EDR CR 1.9, HDS-12 HDR CR 1.9, HDS-12 NDR CR 1.9 |
| FRS-CMP-110 | SVC-02, SDS-9, SDS-12 CR 1.10 | HDS-12 EDR CR 1.10, HDS-12 HDR CR 1.10, HDS-12 NDR CR 1.10 |
| FRS-CMP-111 | SVC-02, SDS-9, SDS-12 CR 1.11 | HDS-12 EDR CR 1.11, HDS-12 HDR CR 1.11, HDS-12 NDR CR 1.11 |
| FRS-CMP-112 | SVC-02, SDS-9, SDS-12 CR 1.12 | HDS-12 EDR CR 1.12, HDS-12 HDR CR 1.12, HDS-12 NDR CR 1.12 |
| FRS-CMP-114 | SVC-02, SDS-9, SDS-12 CR 1.14 | HDS-12 EDR CR 1.14, HDS-12 HDR CR 1.14, HDS-12 NDR CR 1.14 |
| FRS-CMP-201 | SVC-04, SDS-9, SDS-12 CR 2.1 | HDS-12 EDR CR 2.1, HDS-12 HDR CR 2.1, HDS-12 NDR CR 2.1 |
| FRS-CMP-202 | SVC-04, SDS-9, SDS-12 CR 2.2 | HDS-12 EDR CR 2.2, HDS-12 HDR CR 2.2, HDS-12 NDR CR 2.2 |
| FRS-CMP-205 | SVC-04, SDS-9, SDS-12 CR 2.5 | HDS-12 EDR CR 2.5, HDS-12 HDR CR 2.5, HDS-12 NDR CR 2.5 |
| FRS-CMP-206 | SVC-04, SDS-9, SDS-12 CR 2.6 | HDS-12 EDR CR 2.6, HDS-12 HDR CR 2.6, HDS-12 NDR CR 2.6 |
| FRS-CMP-207 | SVC-04, SDS-9, SDS-12 CR 2.7 | HDS-12 EDR CR 2.7, HDS-12 HDR CR 2.7, HDS-12 NDR CR 2.7 |
| FRS-CMP-208 | SVC-04, SDS-9, SDS-12 CR 2.8 | HDS-12 EDR CR 2.8, HDS-12 HDR CR 2.8, HDS-12 NDR CR 2.8 |
| FRS-CMP-209 | SVC-04, SDS-9, SDS-12 CR 2.9 | HDS-12 EDR CR 2.9, HDS-12 HDR CR 2.9, HDS-12 NDR CR 2.9 |
| FRS-CMP-210 | SVC-04, SDS-9, SDS-12 CR 2.10 | HDS-12 EDR CR 2.10, HDS-12 HDR CR 2.10, HDS-12 NDR CR 2.10 |
| FRS-CMP-211 | DD-09, SVC-04, SDS-9, SDS-12 CR 2.11 | HDS-12 EDR CR 2.11, HDS-12 HDR CR 2.11, HDS-12 NDR CR 2.11 |
| FRS-CMP-212 | SVC-04, SDS-9, SDS-12 CR 2.12 | HDS-12 EDR CR 2.12, HDS-12 HDR CR 2.12, HDS-12 NDR CR 2.12 |
| FRS-CMP-301 | SVC-04, SDS-9, SDS-12 CR 3.1 | HDS-12 EDR CR 3.1, HDS-12 HDR CR 3.1, HDS-12 NDR CR 3.1 |
| FRS-CMP-303 | SVC-04, SDS-9, SDS-12 CR 3.3 | HDS-12 EDR CR 3.3, HDS-12 HDR CR 3.3, HDS-12 NDR CR 3.3 |
| FRS-CMP-304 | SVC-04, SDS-9, SDS-12 CR 3.4 | HDS-12 EDR CR 3.4, HDS-12 HDR CR 3.4, HDS-12 NDR CR 3.4 |
| FRS-CMP-305 | SVC-04, SDS-9, SDS-12 CR 3.5 | HDS-12 EDR CR 3.5, HDS-12 HDR CR 3.5, HDS-12 NDR CR 3.5 |
| FRS-CMP-306 | SVC-04, SDS-9, SDS-12 CR 3.6 | HDS-12 EDR CR 3.6, HDS-12 HDR CR 3.6, HDS-12 NDR CR 3.6 |
| FRS-CMP-307 | SVC-04, SDS-9, SDS-12 CR 3.7 | HDS-12 EDR CR 3.7, HDS-12 HDR CR 3.7, HDS-12 NDR CR 3.7 |
| FRS-CMP-308 | SVC-04, SDS-9, SDS-12 CR 3.8 | HDS-12 EDR CR 3.8, HDS-12 HDR CR 3.8, HDS-12 NDR CR 3.8 |
| FRS-CMP-309 | SVC-04, SDS-9, SDS-12 CR 3.9 | HDS-12 EDR CR 3.9, HDS-12 HDR CR 3.9, HDS-12 NDR CR 3.9 |
| FRS-CMP-401 | SVC-09, SDS-9, SDS-12 CR 4.1 | HDS-12 EDR CR 4.1, HDS-12 HDR CR 4.1, HDS-12 NDR CR 4.1 |
| FRS-CMP-402 | SVC-09, SDS-9, SDS-12 CR 4.2 | EN-05, HDS-12 EDR CR 4.2, HDS-12 HDR CR 4.2, HDS-12 NDR CR 4.2 |
| FRS-CMP-403 | SVC-09, SDS-9, SDS-12 CR 4.3 | HDS-12 EDR CR 4.3, HDS-12 HDR CR 4.3, HDS-12 NDR CR 4.3 |
| FRS-CMP-501 | SVC-10, SDS-9, SDS-12 CR 5.1 | HDS-12 EDR CR 5.1, HDS-12 HDR CR 5.1, HDS-12 NDR CR 5.1 |
| FRS-CMP-601 | SVC-04, SDS-9, SDS-12 CR 6.1 | HDS-12 EDR CR 6.1, HDS-12 HDR CR 6.1, HDS-12 NDR CR 6.1 |
| FRS-CMP-602 | SVC-04, SDS-9, SDS-12 CR 6.2 | HDS-12 EDR CR 6.2, HDS-12 HDR CR 6.2, HDS-12 NDR CR 6.2 |
| FRS-CMP-701 | SVC-06, SDS-9, SDS-12 CR 7.1 | HDS-12 EDR CR 7.1, HDS-12 HDR CR 7.1, HDS-12 NDR CR 7.1 |
| FRS-CMP-702 | SVC-06, SDS-9, SDS-12 CR 7.2 | HDS-12 EDR CR 7.2, HDS-12 HDR CR 7.2, HDS-12 NDR CR 7.2 |
| FRS-CMP-703 | SVC-06, SDS-9, SDS-12 CR 7.3 | HDS-12 EDR CR 7.3, HDS-12 HDR CR 7.3, HDS-12 NDR CR 7.3 |
| FRS-CMP-704 | SVC-06, SDS-9, SDS-12 CR 7.4 | HDS-12 EDR CR 7.4, HDS-12 HDR CR 7.4, HDS-12 NDR CR 7.4 |
| FRS-CMP-706 | SVC-06, SDS-9, SDS-12 CR 7.6 | HDS-12 EDR CR 7.6, HDS-12 HDR CR 7.6, HDS-12 NDR CR 7.6 |
| FRS-CMP-707 | SVC-06, SDS-9, SDS-12 CR 7.7 | HDS-12 EDR CR 7.7, HDS-12 HDR CR 7.7, HDS-12 NDR CR 7.7 |
| FRS-CMP-708 | SVC-06, SDS-9, SDS-12 CR 7.8 | HDS-12 EDR CR 7.8, HDS-12 HDR CR 7.8, HDS-12 NDR CR 7.8 |
| FRS-DEV-E204 | SVC-11, SDS-9 | HDS-12 EDR 2.4 |
| FRS-DEV-E213 | SVC-11, SDS-9 | CH-1…4, CP-n-DOOR, PH-02, PH-03, PH-04, HDS-10 ControlLogix 5580, HDS-10 Symbio 800, HDS-10 PowerFlex 755T / FC 102, HDS-12 EDR 2.13 |
| FRS-DEV-E302 | SVC-11, SDS-9 | HDS-12 EDR 3.2 |
| FRS-DEV-E310 | SVC-08, SVC-11, SDS-9 | HDS-12 EDR 3.10 |
| FRS-DEV-E311 | SVC-11, SDS-9 | CP-n-DOOR, PH-01, PH-02, PH-03, HDS-12 EDR 3.11 |
| FRS-DEV-E312 | SVC-11, SDS-9 | HDS-12 EDR 3.12 |
| FRS-DEV-E313 | SVC-11, SDS-9 | HDS-12 EDR 3.13 |
| FRS-DEV-E314 | SVC-11, SDS-9 | HDS-12 EDR 3.14 |
| FRS-DEV-H204 | SVC-11, SDS-9 | HDS-12 HDR 2.4 |
| FRS-DEV-H213 | SVC-11, SDS-9 | NW-06, HS-01, HS-03, HDS-12 HDR 2.13 |
| FRS-DEV-H302 | SVC-05, SVC-11, SDS-9 | HDS-12 HDR 3.2 |
| FRS-DEV-H310 | SVC-08, SVC-11, SDS-9 | HDS-12 HDR 3.10 |
| FRS-DEV-H311 | SVC-11, SDS-9 | HS-04, HDS-12 HDR 3.11 |
| FRS-DEV-H312 | SVC-11, SDS-9 | HS-01, HDS-10 Servers and workstations, HDS-12 HDR 3.12 |
| FRS-DEV-H313 | SVC-11, SDS-9 | HDS-12 HDR 3.13 |
| FRS-DEV-H314 | SVC-11, SDS-9 | ESX-5A, 5B, HS-01, HDS-10 Servers and workstations, HDS-10 Panel PC (OIS-1), HDS-12 HDR 3.14 |
| FRS-DEV-N106 | SVC-10, SDS-9 | PH-06, HDS-12 NDR 1.6 |
| FRS-DEV-N113 | SVC-10, SDS-9 | HDS-12 NDR 1.13 |
| FRS-DEV-N204 | SVC-10, SDS-9 | HDS-12 NDR 2.4 |
| FRS-DEV-N213 | SVC-10, SDS-9 | NW-03, PH-04, HDS-10 Stratix 5800, HDS-10 FortiGate, HDS-12 NDR 2.13 |
| FRS-DEV-N302 | SVC-10, SDS-9 | HDS-12 NDR 3.2 |
| FRS-DEV-N310 | SVC-08, SVC-10, SDS-9 | HDS-12 NDR 3.10 |
| FRS-DEV-N311 | SVC-10, SDS-9 | HS-04, PH-02, HDS-12 NDR 3.11 |
| FRS-DEV-N312 | SVC-10, SDS-9 | HDS-12 NDR 3.12 |
| FRS-DEV-N313 | SVC-10, SDS-9 | HDS-12 NDR 3.13 |
| FRS-DEV-N314 | SVC-10, SDS-9 | HDS-12 NDR 3.14 |
| FRS-DEV-N502 | SVC-10, SDS-9 | HDS-12 NDR 5.2 |
| FRS-DEV-N503 | SVC-10, SDS-9 | HDS-12 NDR 5.3 |
| FRS-DEV-S204 | HIS-04, SDS-9, SDS-12 SAR 2.4 | — |
| FRS-DEV-S302 | HIS-04, SDS-9, SDS-12 SAR 3.2 | — |
| FRS-PLC-001 | SW-02 | — |
| FRS-PLC-002 | SW-07 | HDS-10 ControlLogix 5580 |
| FRS-PLC-003 | SW-09 | — |
| FRS-PLC-004 | SW-03 | — |
| FRS-PLC-005 | SW-07, SW-08 | — |
| FRS-PLC-006 | SW-02 | — |
| FRS-PLC-007 | SW-02 | — |
| FRS-PLC-008 | SW-04, SW-05 | — |
| FRS-PLC-009 | SW-09 | — |
| FRS-PLC-010 | SW-04 | — |
| FRS-PLC-011 | SW-02 | — |
| FRS-PLC-012 | SW-02 | — |
| FRS-PLC-013 | SW-09 | — |
| FRS-PLC-014 | SW-04, SW-09 | — |
| FRS-PLC-015 | SW-01, SW-06 | — |
| FRS-PLC-016 | SW-01, SW-07 | — |
| FRS-PLC-017 | SW-07 | — |
| FRS-PLC-018 | SW-01, SW-07 | — |
| FRS-PLC-019 | SW-07 | — |
| FRS-PLC-020 | SW-02 | — |
| FRS-PLC-021 | SW-10 | — |

# Annex B  Open items to confirm

Carried from URS and FRS Annex D (OI-01 to OI-18) plus:

| ID | Party | Item |
| --- | --- | --- |
| OI-19 | Siemens | Desigo CC V9 supported standby or redundancy configuration for the Z5 server. |
| OI-20 | Vendors | Network ports used by Tracer TU, MCT 10, DeviceCare, ION Setup and TIA Portal secure communication, for rule R-C3-02. |